## SmartAisle
Vertiv™ SmartAisle™ 2 Compliance
Item | Product Type | Category | Specifications | Mandatory | Compliance (Y/N) | Remarks
SmartAisle 2 System
1 | SA | System Provider & Integrator | To state company and provide installation references
2 | SA | Brand | To State
3 | SA | Model | To State
4 | SA | Country Of Origin | To State
5 | SA |  | Entire SmartAisle 2 Solution component include power, cooling, monitoring, HMI, Active Roof, surveillance, motorize door and all relevant sensor come from one single source with fully tested without further on site integration work require | Fully Comply | YES/NO
6 | SA |  | Corridor width | 1200 mm | YES/NO
7 | SA |  | Machine external dimensions | 10200 mm x 3400 mm (bare unit) | YES/NO
8 | Power |  | Power architecture | Centralized power supply | YES/NO
9 | Thermal |  | Cooling architecture | Water Cooled or Air cooled DX based row cooling units, independent cooling modules with Centralize Team Work for Optimize Cooling Control x 4 No. | YES/NO
10 | SA |  | Structured cabling | Column header network wiring closet | YES/NO
11 | Monitoring |  | Fire architecture | External fire, third party mapping provision with Roof opening trigger on Fire Alarm | YES/NO
12 | SA |  | The total number of U-bit single module | 966 (single cabinet 42U, including the network cabinet) | YES/NO
13 | Power |  | Redundant power supply | N+1 | YES/NO
14 | Thermal |  | Redundant cooling | N+1 | YES/NO
15 | Power |  | The average power consumption of a single cabinet | 4 kW | YES/NO
16 | Power |  | IT power consumption single module | 92 kW | YES/NO
17 | Thermal |  | Single refrigeration module | 105 kW | YES/NO
18 | SA |  | Voltage | (380 Vac to 415 Vac ± 10%, 3N ~ | YES/NO
19 | SA |  | Frequency | 50 Hz / 60 Hz | YES/NO
20 | SA |  | Colour | Pantone 877C + RAL7021 | YES/NO
21 | SA |  | The entire architecture of the SmartAisle 2 solution is ISO 9001 certified | Fully Comply | YES/NO
| SA |  | The entire architecture of the SmartAisle is Uptime Tier IV Certified | Fully Comply
22 | SA | Enclosure | The enclosure assembly (Access door & Roof) enables achieving isolation of the hot and cold aisles and provides access control to authorized personnel, and automated roof opening function. | Fully Comply | YES/NO
Vertiv™ SmartAisle™ 2 Compliance
Item | Product Type | Category | Specifications | Mandatory | Compliance (Y/N) | Remarks
23 | SA | Base Construction | The base is constructed from high-grade aluminium with a weight of less than 711 kg. The base is of sturdy construction so that it is able to support the entire weight of the enclosure, equipment and accessories. The base consists of the following components: • 600 mm wide base (28 no.) • 800 mm wide base (2 no.) • The base access door (1 set) • Positioning the base member (6 pieces) | Fully Comply | YES/NO
24 | Rack | Rack Construction | The rack is construct withStandard Color RAL 7021 Powder Coating finishing. The rack holds a static load of up to 1,600 kg. The rack supports 75% open high perforated doors for optimal airflow. The rack has convenient tool-less installation of cable and airflow management, fast deployment leveling feet, and heavy duty caster wheels for easy movement • 42Ux600Wx1100D (6 no.) • 42Ux800Wx1100D (6 no.) | Fully Comply | YES/NO
25 | SA | Access Doors | The access door to the enclosure as of double leaf sliding door type and comprises of an automatic door, glass door (including hanging folders), box door, and the frame structure. | Fully Comply | YES/NO
a | SA | Access Doors | The sliding arrangement of the doors are of two types – 1. Semi- automatic doors – Wherein the opening of the doors is done manually whereas the closing of the doors is done automatically through a motor, gear and guide rail mechanism. 2. Manual doors – The opening and closing of the doors are both manual in operation through a guide rail mechanism and with the help of door handles. | Fully Comply | YES/NO
b | SA | Access Doors | The doors sealing mechanism is through electrically charged magnetic strips which is a part of the access control feature for the entire system. The doors act as a part of containment for the separation of cold aisle and hot aisle which facilitates efficient air movement through the server racks. | Fully Comply | YES/NO
26 | SA | Cable Trunking Passages | The provision of a self-organized and channelizing arrangement for power cabling and control cabling connections should be done to the designated terminals from the power distribution cabinet. There should be cross membered trunking passages located on the top of the cabinet which are assembled at site. Each of the cross membered frames are located to flush conveniently with the cable entry passages inside the cabinet. | Fully Comply | YES/NO
27 | SA | Top Roof Plate | The roof top plate is enclosed in a frame structure which is pivoted at one side. The other side has a mechanism for automatic opening of the roof which is operated by the controller. The opening of the roof top plate facilitates the airflow movement from the rooms across the servers inside the system which only occurs automatically in the event of a fire alarm, power failure or the entire air-conditioning system is shut down. | Fully Comply | YES/NO
Vertiv™ SmartAisle™ 2 Compliance
Item | Product Type | Category | Specifications | Mandatory | Compliance (Y/N) | Remarks
28 | Rack | Server & Network Cabinets | The enclosure is designed to provide a secure, managed environment for computer and networking equipment. It has a minimum of IP20 rating for protection against touch, ingress of foreign bodies. The enclosure also conforms to EIA-310 Standard for Cabinets, Racks, Panels, and Associated Equipment and accommodate industry standard 19” rack mount equipment. Both protect the user from mechanical hazards and generally meet the requirements for a mechanical enclosure (stability, mechanical strength, aperture sizes, etc.) as defined in IEC 60950-1 | Fully Comply | YES/NO
29 | Power | UPS | The UPS is a compact system designed to operate with maximum energy efficiency in a minimum footprint for the protection of small-and-medium computer rooms. | Fully Comply | YES/NO
a | Power | UPS | It features a distinctive technology which incorporates distributed intelligence and scalable power in a common assembly. The UPS system provides complete, high efficient power protection and distribution in a single cabinet, eliminating the complexity of two stage power distribution. | Fully Comply | YES/NO
b | Power | UPS | The UPS has a Modular Power Distribution Module, Hot Swappable Circuit Breaker, Built-in distribution switch and manual maintenance bypass, Standalone static bypass module, Hot swappable module, Unity Power Factor. The UPS system must provide the following features • Single standard rack configuration eliminates the complexity of 2-stage power distribution • High efficiency of 96% at 50% to 75% load, Upto 94% efficiency at 25% & lower loads • Low MTTR without any single point of failure • 110% overload for 60 minutes, 125% for 10 minutes, and 150% for 1 minute | Fully Comply | YES/NO
30 | Power | Power Distribution System | Distribution cabinet power distribution equipment is required to achieve the functionality to provide 19” rack-mount hardware. This system enables to provide metered and precise power requirements of the entire equipment in the system. It should also facilitate timely monitoring of the power modulation that occurs in the entire DC space over the entire operational time thereby creating provisions for managing power across the entire space. It is a single source of power distribution system which facilitates easy cable connection to the end terminal devices. | Fully Comply | YES/NO
Vertiv™ SmartAisle™ 2 Compliance
Item | Product Type | Category | Specifications | Mandatory | Compliance (Y/N) | Remarks
31 | Thermal | Precision Air Conditioning Units | The solution is equipped with the latest technology precision cooling units which are placed within the row of the racks and are designed to deliver high efficiency and availability. It compacts in size to perfectly fit in your changing infrastructure cooling environment. It is ideally suited for rack-level cooling and specifically designed for high return air temperatures together with optimizing air distribution and maximizing efficiency, thereby delivering both cost savings and energy-related savings. The detailed specification of the precision air conditioning system are as follows | Fully Comply | YES
a | Thermal | DC brushless compressor with Rotalock. | The refrigeration circuit of the unit incorporates a high efficiency DC brushless compressor type arrangement with variable capacity operation of 30% to 100% to ensure precise repose to dynamic changing cooling demand and it also has a Rotalock (screw thread) connection mode that makes the maintenance more easier. | Fully Comply | YES
b | Thermal | Heat Exchanger | The heat exchanger is equipped with a fin & tube construction which provides high heat dissipating efficiency. The channels of the exchanger have been designed and tested for specific models, which improve the utilization rate of the heat exchanger. | Fully Comply | YES
c | Thermal | Evaporator Fan | The cooling unit is equipped with highly reliable EC fans, which deliver high efficiency and provide considerable energy savings, space saving at a substantially low noise. These fans are configured to provide a step-less speed regulation over the entire operating range. | Fully Comply | YES
d | Thermal | EEV | The cooling unit is provided with an electronic expansion valve (EEV).The EEV is designed for modulating control of the refrigerant mass flow with precision. The EEV collects temperature and pressure signals at the same time to accurately regulate the refrigerant flow. The EEV's wide operating envelope also lowers down the condensing pressure, thereby resulting significant energy savings. | Fully Comply | YES
e | Thermal | Air Filter | The air filter provided in the return air section of the unit complies to US ASHRAE52-76 and Eurovent 4/5 standards, with a dust resistance value of 90%(EU4 standard). To ensure the normal operation of the filter, the controller is provided with the filter service alarm logic. The default fan running time is 2000 hours (settable according to the local running environment), when the time exceeds, the filter service alarm is triggered. User needs to replace the filter based on the clogging condition of the filter. The filter is checked once a month and replaced as required during operation. | Fully Comply | YES
f | Thermal | Levelling Feet | Vertiv™ Liebert® CRV+ CW air conditioner is installed in the middle of the racks, so at least one side of the unit is on the side of the server cabinet. After each part of the cabinet is installed, the cabinet needs to be leveled which is done by the means of levelling feet installed at the bottom of the unit. | Fully Comply | YES
Vertiv™ SmartAisle™ 2 Compliance
Item | Product Type | Category | Specifications | Mandatory | Compliance (Y/N) | Remarks
g | Thermal | Humidifier | The unit is fitted with an electrode boiler humidifier suitable for use with water of varying degrees of hardness, provided that the water is not treated or demineralized (hardness range < 600 ppm). The humidifier is equipped with a water inlet valve and a maximum water level sensor. The humidifier is provided with a copper steam distributor connecting the cylinder to the evaporating coil that helps mixing the discharge air. The unit controller monitors the condition of the steam cylinder, and generates an alarm when the cylinder needs to be changed; cylinder replacement is easy and quick. The humidifier is provided with a self-adapting flow control system, which monitors and controls the electrical current passing through the cylinder. The output adjustment is 30% to 100% via the unit controller | Fully Comply | YES
h | Thermal |  |  | Fully Comply | YES
i | Thermal |  |  | Fully Comply | YES
j | Thermal |  |  | Fully Comply | YES
k | Thermal | Electrical Heater | The electrical heater consists of heating resistors having a rigid design for extended operational life and are normally utilized to maintain room dry-bulb conditions during a system call for dehumidification. The material of construction for the heater is finned armored stainless steel which is used to maintain a low surface power density. The Ionization effects are eliminated because of the low heater surface temperature. The electrical heater has an ON-OFF type of control. The heater is phase balanced and a manual reset safety thermostat is provided to disable them in the event of a high temperaturee. | Fully Comply | YES
l | Thermal |  |  | Fully Comply | YES
31 | Thermal | Operational Logic for PAC units | With a built-in load sensing logic of operation, the row cooling system senses and delivers the exact amount of conditioned air required by each server rack which provides the most optimum cooling performance as the cooling output quickly adapts to the demands of each rack. Based on the field input devices, the unit operates on a proactive approach to maintain the desired air conditions even during load fluctuations - Minimum of 4 x T&H sensors for temperature and humidity reading at rack level for each cooling unit (for temperature sensing logic). - Share and utilize Monitoring Remote Temperature and Humidity sensors (3 at the front of rack & 1 at the back of rack) to perform optimize thermal control over the thermal teamwork. - Each value, Temperature and Humidity, can independently be enabled for controlling the cooling output. - Differential Sensors are mounted in the calibrated holes which modulate the cooling capacity and airflow. (for pressure sensing logic). - The average or the highest value is calculated in accordance with the number of enabled sensors. | Fully Comply | YES/NO
Vertiv™ SmartAisle™ 2 Compliance
Item | Product Type | Category | Specifications | Mandatory | Compliance (Y/N) | Remarks
32 | SA | HMI Panel | The system is provided with a high end technologically advanced control panel which has a 15” display for viewing the operations and the performance of the entire system. The local display helps administrators or the concerned facility managers by presenting information to achieve the operational objectives of the solution. The controller has futuristic capabilities which display the detailed working of every working component, some of them are mentioned below. | Fully Comply | YES/NO
a | Monitoring | HMI Panel | Thermograph: It Indicates the temperature conditions of the air in both the cold and hot aisles at the top, bottom, and in the central location of each rack. This gives insights of the working of the precision air conditioning system. IT load profile: It describes the present usage of each rack and compares the load profiles with the maximum available capacity for each rack to provide the actual percentage loading as per the current load demands. System alarms: It provides a detailed real time alarms and warning list which is populated and categorized based on the level of criticality. It has a historical storage of 500 alarms in the web browser interface that addresses the urgencies priority-wise. PUE: It specifies the real-time PUE of the entire data center infrastructure by capturing the efficiency of the entire system. | Fully Comply | YES/NO
33 | SA | Auxiliary Light | The auxiliary light or the safety light sensor is mounted on the left and right side of the door entrance bracket frame/posts. It is interlinked with the controller such that in case of an alarm or emergency, the lights get activated which assist in trouble-shooting and problem indication.. | Fully Comply | YES/NO
34 | SA | Lighting Switch / System | The lighting switch is positioned on the door frame at the entrance of the system which assists in the manual operation of the LED lights inside the solution. The switch also acts as an emergency activation of lights in the case of detection of any critical alarms which require immediate attention. | Fully Comply | YES/NO
35 | SA | Sound & Alarm Lights | The sound alarms for critical warnings are coupled with multicolored LED lights inside the system that describes the nature of the alarm with the color of the lights. Red color lights blinking in the system indicate that the alarm is of a critical nature and needs an immediate response from the user. These alarms and lights assist in rapid action to address any issues when the entire system is under a visual inspection personnel at site. | Fully Comply | YES/NO
Vertiv™ SmartAisle™ 2 Compliance
Item | Product Type | Category | Specifications | Mandatory | Compliance (Y/N) | Remarks
36 | Monitoring | Remote Monitoring System | The monitoring system enables the remote supervision of the entire system over a supervisory system (RDU-M) connected to an individual system monitoring (RDU-AG2) kit comprising the entire monitoring architecture of the solution. The RDU-M along with an NVR is mounted on the same rack inside the enclosure assembly. Additionally, there is a provision of an access controller feature mounted on the same IT racks as the RDU-M which comprises of an access card and a door opening function. | Fully Comply | YES/NO
a | Monitoring | Remote Monitoring Feature | In totality, the remote monitoring system shall have the following features • Capable of remote monitoring, controlling, managing Infrastructures (Power, Cooling, and Environment) • Cooling unit’s teamwork management for CRAC units • Provision for real-time alarm and alarm notification by Email / SMS • Alarm Event Actions (Automation) • Data record and event log • Requests only single IP address and offers RJ45 port for sensor “plug-in and play” • Support IPC <= 4 ways and door access management • Support Asset management and warranty reminder • User authorization management • System access management • Support monitoring and management of IT device through IPMI | Fully Comply | YES/NO
b | Monitoring | Temperature & Humidity sensor | The IRM-S02TH temperature and humidity sensor are within the closed cabinet door frame assembly of the system. These standard sensors are fitted uniformly on both sides of the inner channel in the cabinet to ensure the accuracy of measurement throughout the enclosed channel. Each server or network rack is provided with temperature and humidity sensors, three at the front and one at the back. This is to allow the Thermograph image accuracy and to optimize the Thermal Control algorithm performance. The sensor supports MODBUS protocol through RJ45 port in RS-485 mode to configure and collect the data. The LCD display panel displays the sensor address, temperature and humidity data in real time. Temperature and humidity details are displayed by turns every 2 seconds. When the temperature data exceeds the configured setpoints or the sensor fails, the alarm indicator flashes; when the temperature data is in the range of the configured setpoints, the alarm indicator get back to normal. | Fully Comply | YES/NO
f | Monitoring | Infrared Sensor | The infrared sensor is mounted inside the system as a part of the motion detection system. The mounting of the infrared sensors is predetermined with the proper mounting of the base and connection wiring provision is provided at the top part of the system in the channels supporting the roof top plate. | Fully Comply | YES/NO
g | Monitoring | Dome Camera | The dome camera is a part of the surveillance system of the entire solution. It is mounted on the entrance door assembly and provides a continuous view of the entire accessibility to the system. The mounting base and cover are properly fitted onto the dome camera to ensure rigidity and proper functioning. Vertiv Dome camera comes with 1.3 MP (1280×960) and 2.0 MP (1920×1080) in progressive scan CMOS format, with H.264 video compression. | Fully Comply | YES/NO
Vertiv™ SmartAisle™ 2 Compliance
Item | Product Type | Category | Specifications | Mandatory | Compliance (Y/N) | Remarks
h | Monitoring | Dome Camera | The network camera provides true and day-night (ICR) low-light capabilities with sensitivity down to 0.01 Lux @ (F1.2, AGC ON), 0 Lux with IR; 0.028 Lux @ (F2.0, AGC ON), 0 Lux with IR. It supports Back Llight Compensation (BLC) with selectable zones. The camera offers video compression of H.264, MJPEG. Dual H.264 streams are supported with independent resolution, bit rate and frame rates for the main and sub streams.The network camera shall include embedded Linux OS and support IE and client software for network preview, and is capable of performing firmware upgrades through a network using a software-based device utility or through the web interface. The camera provide the ability to take snapshot and record. The network camera supports standard IT protocols including: TCP/IP, HTTP, DHCP, DNS, DDNS, RTP, RTSP, PPPoE, SMTP, NTP, UPnP, ICMP, IGMP, SNMP, FTP, QoS.and it also supports industry standard Power over Ethernet (PoE) IEEE 802.3af for powering the camera over the network in addition to 12 Vdc local power supply | Fully Comply | YES/NO
j | Monitoring | Finger Print Reader | The access to the SmartAisle system should be done through a finger print scanner mechanism that enables only a selected group of authorized personnel to enter the SmartAisle. This scanner should be linked to the Remote monitoring system so as to provide the user fully authority to grant or restrict access to the SmartAisle based on the criticality of any threatening scenario for the system. | Fully Comply | YES/NO
k | Monitoring | Finger Print Reader | The scanner comes with identification authorization confirmation functions, supports Wiegand 26 output and RS 485. Features or the scanner are as below: - Dimension: 155mm(L) * 52mm(W) * 39mm(D) ±5%; Weight: 0.2Kg±5%; Working Voltage: 12VDC±5%; Working Current: 300mA±5%; Frequency: ID card: 125KHZ±5%, IC card: 13.56MHZ±5%; Reading distance: 50-100mm (without other same products interferences); Working environment: -10~+55 C degree, 20%~90%; Working environment: -20~+70℃, 5%～90%; ESD parameter: air discharge ±8KV Keypad: 12 keys Working status: standby status, LED blue light ON; scan the fingerprint, green LED light ON; illegal fingerprint, buzzer three beeps, red LED and blue LED blink twice; legal fingerprint, buzzer beep once, red LED and blue LED blinks twice; legal fingerprint, buzzer beep once, red LED light and blue LED light blink once; swipe card, buzzer beep once, red LED light and blue light blink once. | Fully Comply | YES/NO
SmartAisle 2 Compliance
Item | Product Type | Category | Specifications | Mandatory | Compliance (Y/N) | Remarks
| Monitoring | Face Recognition Reader | The access to the SmartAisle system should be done through a Face recognition mechanism that enables only a selected group of authorized personnel to enter the SmartAisle. | Fully Comply | YES/NO
| Monitoring | Face Recognition Reader | Equipment performance Infrared, RGB dual camera dynamic anti-counterfeiting, completely solve the deception of various photos on various carriers;99.99% accuracy rate (99.77% recognition pass rate at 1% false recognition rate; recognition pass rate at 0.1% false recognition rate(99.27% rate) The device can store face records locally (a)The cloud platform device supports the simultaneous storage of 50,000 face photos (less than 400KB) and 1 million recognition records(0.45KB), 100,000 live snapshot photos; (b) LAN device supports storage of 50,000 face photos at the same time Film (the photo is calculated based on 100KB), 1 million identification records (including the latest 10,000 live snapshot photos). Fast recognition speed The recognition speed is less than 1 second. Secondary development (can be integrated) Support HTTP interface docking; support 232 serial port output, Wiegand 26, 34 output, the output content can be Custom configuration. High scalability Support public network and local area network deployment; support screen display content configuration; support swipe card. | Fully Comply | YES/NO
Vertiv™ SmartAisle™ 2 Compliance
Item | Product Type | Category | Specifications | Mandatory | Compliance (Y/N) | Remarks
37 | Rack PDU | Rack Mount PDU | The Server Rack shall come with Rack Mount PDU, this PDU shall have :
locking socket - without the need of propriety power cord
upgradeable module when customer wants metering and/or remote monitoring
5 - year warranty
color chassis to differentiate A and B Sources
color differentiation for circuit 1 and 2
low profile breakers
support environmental sensor
38 | Rack | Intelligent Access Control Cabinet Lock | Eack rack shall have built in electronic intelligent locks that can be controlled by proximity smart card to open locks.
Access Control Functions Access Control Authorized: max 512pcs ID card; Software Authorized: using software to authorize Events Records: max 1120pcs RS485 network real-time monitoring, door status, handles state,live Time function; Emergency mechanical key lock function
Door open method Swipe card to open; Remote control to open; Mechanical keys to open.
Device Parameters: Color: Black; Working Voltage: 12VDC±5％ Input Voltage Range:10.8VDC－13.2VDC; RF working frequency: 125KHZ±5% ; Swiping card distance: 20-50mm; Working status: Normal power flashed green and red, the lamp stand, access control alarm flashing red light, legally unlock the green light till the lock open, illegal to swipe card, red light blinks;